## Slide 1: Neural Network Assisted Temporal Reduction for Transmission Expansion Planning

## Slide 2: Overview
Problem setting + motivation (2-3)
Methodology
  Process overview (1)
  Optimization problem (2)
  Neural network (2)
  Line benefits (1)
  Clustering process (1)
Results thus far
  Neural network output (6)
  Line benefits (2)
Future tasks (1)

## Slide 3: Problem setting
Research background
Transmission expansion planning (TEP) is based on calculating Optimal Power Flow (OPF)
OPF problem is computationally heavy, especially AC formulations
Temporal aggregation for problem size reduction
Clustering for representative periods
How to find representative days for a spatially resolved system?
Ex-post clustering
Multitude of OPFs have to be solved for Transmission Expansion Planning
  Multiple investment candidates (lines)
  Multiple discrete investment quantities
  Weather year sensitivity
Might still be computationally intensive
Literature shows that ML methods can accurately approximate OPF results very fast

## Slide 4: Background: transmission expansion planning
TEP is based on calculating the demanding OPF problem
Increasing share of renewables  Rising variability in system operation
Temporal reduction techniques  Representative periods
Capture variability in system operating conditions (weather)
Accurately represent physical constraints of network
Many demanding OPFS
Computational tractability
Temporal reduction
Representative periods

## Slide 5: Motivation: finding representative periods
How to find representative periods for a spatially resolved system with complex interactions?
 Ex-post clustering = use simplified model to extract features relevant for your problem and cluster on those

## Slide 6: Motivation: finding representative periods
Proposed feature for clustering for TEP: Investment benefit of individual lines
  Many possible candidates
  Many discrete values for expansion
  Weather year sensitivity
A multitude of OPFs to be solved
Replace part of the calculation with a machine-learning algorithm

## Slide 7: Process overview
*ESOM: Energy System Optimization Model
**ANN: Artificial Neural Network
ESOM
ESOM
Input Data
Representative Time Series
ESOM
Representative Time Series
Relaxed ESOM
Benchmark:
Full time horizon
Traditional:
Split time horizon
Based in Costs:
Split time horizon
Features
(Investment benefit)
ESOM
Representative Time Series
Proposal:
Split time horizon
ANN: Cost Estimator
Investment Benefit
Features
Input Time Series
(ANN + Kmedoids)
Clustering
Method
Clustering
Method
Clustering
Method

## Slide 8: ESOM: Transmission Expansion Planning considering AC-OPF
Minimize: |  |  | (1.1)
With constraints: |  |  | 
 |  |  | (1.2)
 |  |  | (1.3)
 |  |  | (1.4)
 |  |  | (1.5)
 |  |  | (1.6)
 |  |  | (1.7)
 |  |  | (1.8)
 |  |  | (1.9) (1.10)
Minimize: |  |  | (1.1)
With constraints: |  |  | 
 |  |  | (1.2)
 |  |  | (1.3)
 |  |  | (1.4)
 |  |  | (1.5)
 |  |  | (1.6)
 |  |  | (1.7)
 |  |  | (1.8)
 |  |  | (1.9) (1.10)
Non-convex
Getting a MILP model by applying:
Disjunctive constraints
Piecewise functions
McCormick envelopes

## Slide 9: ESOM: Why considering AC-OPF?
RTS-GMLC
Source: Scenario Creation and Power Conditioning Strategies for
Operating Power Grids with Two-Stage Stochastic Economic Dispatch
Link: https://www.nrel.gov/docs/fy21osti/75363.pdf
Implications on the Gen. capacity planning
Implications on the transmission expansion
Disadvantages:
ACOPF’s problem size is ~4x-6x of the DCOPF
Computation burden: ~6x-10x

## Slide 10: Line Benefits
Reference grid
ANN Cost
Estimator
ANN Cost
Estimator
Benefit 1 (Benefit 2) =
Reference grid – PINT
(TOOT – Reference grid)
Sequence per candidate asset and hour
The PINT and TOOT
Line Benefit Methods:
The Put IN one at the Time (PINT)
The Take Out One at the Time (TOOT)
Shapley value
Aumann-shapley value
[source] ENTSO-E: Guideline for Cost Benefit Analysis of Grid Development Projects
Link: https://eepublicdownloads.entsoe.eu/clean-documents/tyndp-documents/Cost%20Benefit%20Analysis/191023_CBA3_Draft%20for%20consultation.pdf
ANN: Cost Estimator
Investment Benefit
PINT (or TOOT)

## Slide 11: Clustering process
Dimensionality reduction
Optimal number of representatives/clusters
Selection/aggregation using K-medoids
Dimensionality reduction using PCA
Optimal number of clusters:
Elbow method

## Slide 12: Line Benefits: Preliminary results